## ITP - Structural
INSPECTION & TEST PLAN — STRUCTURAL DISCIPLINE
PROJECT | [Project Name] | CONTRACT | [XXX-XXX] | REV | [0] | DATE | [DD/MMM/YYYY] | PREPARED | [Name] | APPROVED | [Name]
LEGEND | HOLD | Mandatory stop | WITNESS | Inspector invited | REVIEW | Document review
WBS / Item ID | Project Phase | Discipline | Inspection Category | Inspection Point | Acceptance Criteria | Code Reference (SBC/US) | Responsible Party | Frequency | Intervention Type (H/W/R) | Status (Pass/Fail/NA) | Remarks / NCR Ref.
PRE-CONSTRUCTION
STR-PRE-001 | Pre-Construction | STR | Material Verification | ISO 17025 Lab Accreditation | Verify 3rd-party testing agency holds SASO/ISO 17025 accreditation for specific project tests (slump, compressive, NDT). | ISO 17025 | QA Manager | Pre-Task | Review
STR-PRE-002 | Pre-Construction | STR | Mix Design | Durability & Chloride Limits | Verify concrete mix proportions meet design strength, maximum water-to-cement ratio, and strict chloride/sulfate limits. | ACI 318 Ch. 19 | Site Engineer | Per Mix | Review
STR-PRE-003 | Pre-Construction | STR | Steel Erection | WPS & Welder Qualifications | Welding Procedure Specifications (WPS) and welder certifications reviewed and approved for project-specific positions. | AWS D1.1 | Welding Insp. | Pre-Task | Review
EXECUTION
STR-EXE-001 | Execution (Pre-Pour) | STR | Site Preparation | Hot Weather Mitigation Plan | Verify chilled water/ice batching, evaporative retarders, and sun shading are active for pours exceeding 32°C (90°F). | ACI 305R / SBC 304 | Site Sup. | Per Pour | Hold
STR-EXE-002 | Execution (Pre-Pour) | STR | Formwork & Rebar | Mechanical Splicing (Couplers) | Verify torque and thread engagement for mechanical couplers in congested high-rise zones; verify staggered lap splices. | ACI 318 Ch. 25 | QC Inspector | Per Element | Hold
STR-EXE-003 | Execution (Active) | STR | Concrete Placement | SCC Slump Flow & Temperature | Perform slump flow (spread) test for Self-Consolidating Concrete; verify delivery temperature is within approved limits. | ASTM C1611 / ACI 237R | Lab Tech | Per Truck | Hold
STR-EXE-004 | Execution (Active) | STR | Concrete Placement | Placement & Consolidation | Ensure no segregation, proper continuous consolidation, and correct drop heights using approved equipment. | ACI 309R | Site Engineer | Continuous | Witness
STR-EXE-005 | Execution (Active) | STR | Steel Erection | Bolt Pre-Tensioning Verification | Verify Turn-of-Nut, Calibrated Wrench, or DTI Washers for slip-critical joints. Torque alone is rejected. | AISC 360 / RCSC | QC Inspector | Per Joint | Hold
STR-EXE-006 | Execution (Active) | STR | Steel Erection | Base Plate Grouting | Verify dry-packing or pouring of approved non-shrink grout beneath column base plates. | ASTM C1107 | Site Sup. | Per Column | Hold
STR-EXE-007 | Execution (Active) | STR | Steel Erection | Field Welding | Field welds comply with visual quality standards; no surface cracks, undercut, or porosity. | AWS D1.1 | Welding Insp. | Per Joint | Witness
POST-EXECUTION
STR-PST-001 | Post-Execution | STR | Curing | Moisture Retention | Water curing or approved curing membrane applied immediately after finishing, maintained for a minimum of 7 days. | ACI 308R | Site Engineer | Daily | Witness
STR-PST-002 | Post-Execution | STR | Surface Inspection | Surface Defects & Finish | Formwork removed without damage; no honeycombing, severe shrinkage cracks, or out-of-tolerance irregularities. | ACI 301 | QC Inspector | Post-Strip | Hold
STR-PST-003 | Post-Execution | STR | Testing | Compressive Strength | Cylinders/cubes meet design 28-day strength. Root Cause Analysis (RCA) triggered immediately if failed. | ASTM C39 | Lab Tech | 7/28 Days | Review
STR-PST-004 | Post-Execution | STR | Testing | Weld Testing (NDT) | Ultrasonic Testing (UT), Radiographic Testing (RT), or Magnetic Particle (MT) on critical welds show no discontinuities. | AWS D1.1 | QC Inspector | Per Specs | Review
STR-PST-005 | Post-Execution | STR | Structural Alignment | Frame Plumbness & Level | Structural steel frame plumbness, level, and squareness verified within code tolerances. | AISC Code of Standard Practice | Site Engineer | Post-Erect | Hold
DOC. NO. | [ITP-STR-001] | STATUS | For Construction | CLASSIFICATION | Quality Controlled Document |  |  | Page | 1 of 1